Pos:  Knürr® Miracel2 server cabinet:

Dismountable universal stand made from extruded aluminum sections consisting of inserted aluminum die cast corner connections and horizontal and vertical aluminum sections with circumferential T grooves for the attachment of cabinet accessories, cable guides, rails, bars and other accessories. Cable inlets possible through cover and base. Cabinets may be stacked side by side, without side plates if required.

The cabinets are compatible with a similar heavy-duty cabinet with a bearing load of up to 1,500kg and its accessories.

The 19" extrusions section models according to IEC 297-3 are available as server or breadboard sections with U dimensions consisting of steel panels and as aluminum T-grooves to house spring nuts. The depth of the 19" sections can be adjusted continuously in the front and rear of the cabinet.

The front and rear doors are perforated over a large area for a high air flow rate (83% free space) and comprise three hinges per door with a 160° opening angle (individual cabinet) with a 180° opening angle available as an option. Both doors have a three-point or four-point locking system with a lever for the inclusion of a closing cylinder or security lock. The doorstop can

be changed on site. The doors may be assembled either on the front or rear of the cabinet. 160° doors may be dismantled and assembled without tools. The doors are also available as double-wing glass or steel sheet doors, with or without perforation.

Top cover: with rear cable inlet consisting of 3 plastic sliding plates (UL094V0) to be opened fully to allow for assembly or dismantling of cover after cabling. The cable inlet has a minimum opening of 435x115mm and can be fully dismantled. The cable inlets are also available in the form of brush strips at the front, or on the left and right. Side panels: may be mounted in the T-groove of the base frame and attached with quick release fasteners in the vertical T-grooves of the cabinet, or may be screwed onto the cabinet frame, earthed and prepared for closing cylinders.

The optional bottom plates may comprise cable inlets with foam rubber seals or brush strips and may either be perforated or available as a closed design.

The bottom plates consist of several sections so that the cable inlets can be positioned individually.

The cabinet may be equipped with cable managers covering the entire height which are available in vertical and horizontal (19") designs. The vertical cable managers comprise 3 cable ducts which may be covered with bush strips or blanking plates.

The entire height of the cabinet front may be fitted with air partitioning steel sheets for the partitioning of the internal air. The latter are available with additional 3x 19" 1HE vertical sections which are covered with blanking plates. The air partitioning steel sheets can be adjusted continuously with the front 19" sections.

A series of cabinets with air partitioning may also be available without side sections. Partition panels may be assembled afterwards between these cabinets in order to separate them.

Additional components such as doors, side sections, covers and bases are earthed by means of earth conductors according to DIN EN 60950 and VDE 0100 T450.

Loading capacity 8000 N static.

Protection type. IP-20 EN60529

Verifications: Earthing according to VDE 0100 T 540. DIN EN 60950.

Material / surface:

Base frame: Aluminum

Cover parts: galvanized steel sheet, powder-coated structure.

Doors: Steel sheet, powder-coated structure.

19” galvanized steel sheet section, 2 mm.

Scope of delivery:

1 x aluminum base frame

4 x 19” steel sheet server extrusions with U-labeling for the assembly of standard 19" servers.

2 x side panels with quick release fasteners.

1 x top cover with rear cable inlet (three-part sliding plate to be opened fully).

1 x single-leaf perforated front door with a lever for the inclusion of a closing cylinder.

1 x single-leaf perforated rear door with a lever for the inclusion of a closing cylinder.

1 x complete earthing set (VDE 0100).

4 x leveling feet.

Installation height: 2095 mm, 47 U

Cabinet dimensions:

Height:   2191 mm

Width:   600 mm

Depth:   1000 mm

Weight:  91kg

Maneuvering room: from door to 19" section = 80 mm

Maneuvering room: between 19" front / rear sections 740mm

Color of cover parts RAL 7035 light gray =.1 or .RAL 7021 =.8 dark gray. Instead of .x in the order number

Delivery status: Fully mounted, screwed onto disposable pallet with lightweight packaging

Manufacturer: Knürr GmbH

Type: Miracel2 – server cabinet

Item number: 01.157.007.x.036

or equivalent

Unit    Quantity    Unit price (UP)    Total price (TP)

_____     _____     ___________        ______________